## 1 พัดลม
[6 empty] | Software version : | Rel. 1.0.1.0
[6 empty] | Date : | 2024-04-18
Project :
Quotation :
Air Cooler |  | Technical specifications ‐ Model : |  |  |  | KA-4001-9EB
Series : | KA
Capacity Information | [8 empty] | Model | Electrical Defrosing |  |  |  | Size |  |  |  |  | Surface | Tube volume | Axial fan | [7 empty] | Connection |  | Fin Spacing | Price
Refrigerant |  |  | R404A |  | Surface |  | 10.66 | m2 |  | Coil | Water tray | amount | TA…7 | L | B | H | D | E1 |  |  | Air Flow | Distance | Fan Speed | Diameter | Noise Level in 3M | Voltage | Input Power | Current | Liquid | Gas
Capacity |  |  | 4.7 | KW | Tube Volume |  | 4.2 | L |  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W
Room Temp |  |  | 10 | °C | Fin Pitch |  | 9 | mm | KA-4001-7EB | 3x690 | 1X690 | 2760 | 37 | 1024 | 346 | 532 | 412 | 779 | 13 | 4.2 | 3320 | 9 | 1430 | 400 | 77 | 220V/1PH | 160 | 0.7 | 1/2" | 1-1/8" | 7 | 27000
Evaporation temp |  |  | 0 | °C | Test Pressure |  | 30 | Bar | KA-4001-7EC | 4x725 | 1X725 | 3625 | 39.5 | 1024 | 412 | 532 | 412 | 779 | 20 | 6.3 | 3080 | 8 | 1430 | 400 | 77 | 220V/1PH | 160 | 0.7 | 1/2" | 1-1/8" | 7 | 32000
Superheating |  |  | 5 | K |  |  |  |  | KA-5001-7EB | 4x880 | 1X880 | 4400 | 62.5 | 1275 | 425 | 680 | 491 | 1030 | 23 | 7.6 | 7250 | 18 | 1325 | 500 | 83 | 380V/3PH | 820 | 1.59 | 5/8" | 1-3/8" | 7 | 46000
Condensation temp |  |  | 45 | °C |  |  |  |  | KA-5001-7EC | 6x920 | 2X920 | 7360 | 69.5 | 1275 | 491 | 680 | 491 | 1030 | 35 | 11.1 | 6880 | 17 | 1325 | 500 | 83 | 380V/3PH | 820 | 1.59 | 5/8" | 1-3/8" | 7 | 56000
Suction gas temp |  |  | 20 | °C |  |  |  |  | KA-4001-9EB | 3x690 | 1X690 | 2760 | 37 | 1024 | 346 | 532 | 412 | 779 | 10.66 | 4.2 | 3520 | 10 | 1430 | 400 | 77 | 220V/1PH | 160 | 0.7 | 1/2" | 1-1/8" | 9 | 28000
Subcooling |  |  | 0 | K |  |  |  |  | KA-4001-9EC | 4x725 | 1X725 | 3625 | 39.5 | 1024 | 412 | 532 | 412 | 779 | 15.87 | 6.3 | 3320 | 9 | 1430 | 400 | 77 | 220V/1PH | 160 | 0.7 | 1/2" | 1-1/8" | 9 | 32000
[9 empty] | KA-5001-9EB | 4x880 | 1X880 | 4400 | 62.5 | 1275 | 425 | 680 | 491 | 1030 | 18.9 | 7.6 | 7550 | 19 | 1325 | 500 | 83 | 380V/3PH | 820 | 1.59 | 5/8" | 1-3/8" | 9 | 46000
Fan Specification | [8 empty] | KA-5001-9EC | 6x920 | 2X920 | 7360 | 69.5 | 1275 | 491 | 680 | 491 | 1030 | 28.23 | 11.1 | 7020 | 18 | 1325 | 500 | 83 | 380V/3PH | 820 | 1.59 | 5/8" | 1-3/8" | 9 | 56000
Air Flow |  |  | 3520 | m3/h | Voltage |  | 220V/1PH
Air Throw (approx) |  |  | 10 | m | Fan Speed |  | 1430 | rpm
Fan Diameter |  |  | 400 | mm | Power |  | 160 | W | Air Inlet | A: 18; B: 10; C: 5; D: 0; E: -5; F: -10; G: -18; H: -25
Number of Fan |  |  | 1 |  | Current |  | 0.7 | Amp | Evap Temp | A: 6; B: 0; C: -3; D: -8; E: -12; F: -17; G: -25; H: -31
[5 empty] | Noise Level 3 m |  | 77 | dBA | bar: A to H
[9 empty] | KA-4001-7EB | A: 746; B: 6.22; C: 4.976; D: 4.385; E: 3.82; F: 3.689; G: 3.48
[9 empty] | KA-4001-7EC | A: 9.27; B: 7.73; C: 6.192; D: 5.456; E: 4.753; F: 4.591; G: 4.33
Tube Material |  |  | Copper |  | Inlet connection |  | 1/2" | inch | KA-5001-7EB | A: 13.66; B: 11.38; C: 9.11; D: 8.02; E: 6.99; F: 6.75; G: 6.37
Fin Material |  |  | Aluminum |  | Outlet connection |  | 1-1/8" | inch | KA-5001-7EC | A: 17.29; B: 14.42; C: 11.53; D: 10.15; E: 8.84; F: 8.54; G: 8.06
Casing Material |  |  | Powder-coated |  | Dry weight |  | 37 | kg | KA-4001-9EB | A: 5.53; B: 4.7; C: 3.95; D: 3.78; E: 3.42; F: 3.36; G: 3.23; H: 2.61
[9 empty] | KA-4001-9EC | A: 6.95; B: 5.91; C: 4.96; D: 4.74; E: 4.29; F: 4.22; G: 4.06; H: 3.28
Dimension : | [8 empty] | KA-5001-9EB | A: 10.73; B: 9.12; C: 7.69; D: 7.34; E: 6.63; F: 6.53; G: 6.27; H: 5.06
L : | 1024 | [7 empty] | KA-5001-9EC | A: 13.78; B: 11.71; C: 9.88; D: 9.43; E: 8.52; F: 8.39; G: 8.06; H: 6.5
E1 : | 779
H : | 532
W : | 346
B : | 412
Defrost
Electric Defrost for Coil |  |  | 3x690 | W |  | Drainage | G 1"
Electric Defrost for Tray |  |  | 1X690 | W |  | Price | 28000
Total |  |  | 2760 | W

## 2 พัดลม
[6 empty] | Software version : | Rel. 1.0.1.0
[6 empty] | Date : | 2024-04-18
Project :
Quotation :
Air Cooler |  | Technical specifications ‐ Model : |  |  |  | KA-5002-9EB
Series : | KA
Capacity Information | [8 empty] | Model | Electrical Defrosing |  |  |  | Size |  |  |  |  | Surface | Tube volume | Axial fan | [8 empty] | Connection |  | Fin Spacing | Drainage | Price
Refrigerant |  |  | R404A |  | Surface |  | 37.8 | m2 |  | Coil | Water tray | amount | TA…7 | L | W | H | B | E1 |  |  | Air Flow | Distance | Fan Speed |  | Diameter | Noise Level in 3M | Voltage | Input Power | Current | Liquid | Gas
Capacity |  |  | 12.54 | KW | Tube Volume |  | 14.3 | L |  | A | B | C | D | E | F | G | H | I | J | K | L | M | N |  | O | P | Q | R | S | T | U | V | W | X
Room Temp |  |  | -18 | °C | Fin Pitch |  | 9 | mm | KA-3002-7EA | 2x1070 | 1X1070 | 3210 | 42 | 1474 | 424 | 452 | 342 | 1229 | 13 | 4.1 | 2900 | 9 | 1380 | 2 | 300 | 73 | 220V/1PH | 62 | 0.28 | 1/2" | 1-1/8" | 7 | G1" | 30000
Evaporation temp |  |  | -25 | °C | Test Pressure |  | 30 | Bar | KA-3002-7EB | 2x1070 | 1X1070 | 3210 | 44 | 1474 | 424 | 452 | 342 | 1229 | 17 | 5.5 | 2840 | 8 | 1380 | 2 | 300 | 73 | 220V/1PH | 62 | 0.28 | 1/2" | 1-1/8" | 7 | G1" | 33000
Superheating |  |  | 5 | K |  |  |  |  | KA-3502-7EB | 3x1300 | 1X1300 | 5200 | 61 | 1774 | 514 | 532 | 412 | 1529 | 26 | 8.2 | 5560 | 11 | 1400 | 2 | 350 | 75 | 220V/1PH | 130 | 0.58 | 5/8" | 1-3/8" | 7 | G1.5" | 40000
Condensation temp |  |  | 45 | °C |  |  |  |  | KA-4002-7EB | 3x1300 | 1X1300 | 5200 | 63 | 1774 | 514 | 532 | 346 | 1529 | 26 | 8.2 | 6640 | 13 | 1430 | 2 | 400 | 80 | 220V/1PH | 160 | 0.7 | 5/8" | 1-3/8" | 7 | G1.5" | 45000
Suction gas temp |  |  | 20 | °C |  |  |  |  | KA-4002-7EC | 4x1300 | 1X1300 | 6500 | 80.5 | 1774 | 514 | 532 | 412 | 1529 | 39 | 12.1 | 6160 | 12 | 1430 | 2 | 400 | 80 | 220V/1PH | 160 | 0.7 | 5/8" | 1-3/8" | 7 | G1.5" | 58000
Subcooling |  |  | 0 | K |  |  |  |  | KA-5002-7EB | 4x1685 | 1X1685 | 8425 | 102.5 | 2295 | 594 | 680 | 425 | 2030 | 46 | 14.3 | 14500 | 23 | 1325 | 2 | 500 | 86 | 380V/3PH | 820 | 1.59 | 7/8" | 1-3/8" | 7 | G1.5" | 84000
[9 empty] | KA-5002-7EC | 6x1685 | 2X1685 | 13480 | 123.5 | 2295 | 594 | 680 | 491 | 2030 | 69 | 21.5 | 13760 | 22 | 1325 | 2 | 500 | 86 | 380V/3PH | 820 | 1.59 | 7/8" | 1-5/8" | 7 | G1.5" | 105000
Fan Specification | [8 empty] | KA-3002-9EA | 2x1070 | 1X1070 | 3210 | 42 | 1474 | 424 | 452 | 342 | 1229 | 10.66 | 4.1 | 3000 | 9 | 1380 | 2 | 300 | 73 | 220V/1PH | 62 | 0.28 | 1/2" | 1-1/8" | 9 | G1" | 30000
Air Flow |  |  | 15100 | m3/h | Voltage |  | 380V/3PH |  | KA-3002-9EB | 2x1070 | 1X1070 | 3210 | 44 | 1474 | 424 | 452 | 342 | 1229 | 14.16 | 5.5 | 2960 | 8 | 1380 | 2 | 300 | 73 | 220V/1PH | 62 | 0.28 | 1/2" | 1-1/8" | 9 | G1" | 33000
Air Throw (approx) |  |  | 23 | m | Fan Speed |  | 1325 | rpm | KA-4002-9EB | 3x1300 | 1X1300 | 5200 | 63 | 1774 | 514 | 532 | 346 | 1529 | 21.23 | 8.2 | 7040 | 13 | 1430 | 2 | 400 | 80 | 220V/1PH | 160 | 0.7 | 5/8" | 1-3/8" | 9 | G1.5" | 45000
Fan Diameter |  |  | 500 | mm | Power |  | 820 | W | KA-4002-9EC | 4x1300 | 1X1300 | 6500 | 80.5 | 1774 | 514 | 532 | 412 | 1529 | 31.66 | 12.1 | 6640 | 12 | 1430 | 2 | 400 | 80 | 220V/1PH | 160 | 0.7 | 5/8" | 1-3/8" | 9 | G1.5" | 58000
Number of Fan |  |  | 2 |  | Current |  | 1.59 | Amp | KA-5002-9EB | 4x1685 | 1X1685 | 8425 | 102.5 | 2295 | 594 | 680 | 425 | 2030 | 37.8 | 14.3 | 15100 | 23 | 1325 | 2 | 500 | 86 | 380V/3PH | 820 | 1.59 | 7/8" | 1-3/8" | 9 | G1.5" | 84000
[5 empty] | Noise Level 3 m |  | 86 | dBA | KA-5002-9EC | 6x1685 | 2X1685 | 13480 | 123.5 | 2295 | 594 | 680 | 491 | 2030 | 56.39 | 21.5 | 14040 | 22 | 1325 | 2 | 500 | 86 | 380V/3PH | 820 | 1.59 | 7/8" | 1-5/8" | 9 | G1.5" | 105000
Tube Material |  |  | Copper |  | Inlet connection |  | 7/8" | inch
Fin Material |  |  | Aluminum |  | Outlet connection |  | 1-3/8" | inch
Casing Material |  |  | Powder-coated |  | Dry weight |  | 102.5 | kg
[9 empty] | Air Inlet | A: 18; B: 10; C: 5; D: 0; E: -5; F: -10; G: -18; H: -25
Dimension : | [8 empty] | Evap Temp | A: 6; B: 0; C: -3; D: -8; E: -12; F: -17; G: -25; H: -31
L : | 2295 | bar: A to H
E1 : | 2030 | [7 empty] | KA-3002-7EA | A: 6.34; B: 5.28; C: 4.23; D: 3.73; E: 3.24; F: 3.13; G: 2.96
H : | 680 | [7 empty] | KA-3002-7EB | A: 7.66; B: 6.38; C: 5.11; D: 4.49; E: 3.91; F: 3.78; G: 3.57
W : | 594 | [7 empty] | KA-3502-7EB | A: 10.3; B: 9.1; C: 7.7; D: 6.81; E: 5.93; F: 5.73; G: 5.42
B : | 425 | [7 empty] | KA-4002-7EB | A: 14.83; B: 12.36; C: 9.89; D: 8.71; E: 7.59; F: 7.33; G: 6.92
[9 empty] | KA-4002-7EC | A: 18.37; B: 15.31; C: 12.25; D: 10.79; E: 9.41; F: 9.08; G: 8.57
[9 empty] | KA-5002-7EB | A: 26.59; B: 22.16; C: 17.73; D: 15.66; E: 13.64; F: 13.17; G: 12.43
[9 empty] | KA-5002-7EC | A: 34.33; B: 28.62; C: 22.89; D: 20.17; E: 17.57; F: 16.97; G: 16.01
[9 empty] | KA-3002-9EA | A: 5.37; B: 4.56; C: 3.85; D: 3.67; E: 3.31; F: 3.26; G: 3.14; H: 2.53
Defrost | [8 empty] | KA-3002-9EB | A: 6.15; B: 5.23; C: 4.41; D: 4.21; E: 3.8; F: 3.74; G: 3.6; H: 2.9
Electric Defrost for Coil |  |  | 4x1685 | W |  | Drainage | G1.5" |  | KA-4002-9EB | A: 11.02; B: 9.37; C: 7.91; D: 7.54; E: 6.81; F: 6.71; G: 6.45; H: 5.2
Electric Defrost for Tray |  |  | 1X1685 | W |  | Price | 84000 |  | KA-4002-9EC | A: 13.89; B: 11.8; C: 9.96; D: 9.51; E: 8.58; F: 8.45; G: 8.12; H: 6.55
Total |  |  | 8425 | W |  |  |  |  | KA-5002-9EB | A: 21.43; B: 18.22; C: 15.37; D: 14.66; E: 13.24; F: 13.04; G: 12.54; H: 10.11
[9 empty] | KA-5002-9EC | A: 27.54; B: 23.41; C: 19.74; D: 18.84; E: 17.02; F: 16.76; G: 16.11; H: 12.99

## 3 พัดลม
[6 empty] | Software version : | Rel. 1.0.1.0
[6 empty] | Date : | 2024-04-18
Project :
Quotation :
Air Cooler |  | Technical specifications ‐ Model : |  |  |  | KA-5003-7EB
Series : | KA
Capacity Information | [8 empty] | Model | Electrical Defrosing |  |  |  | Size | [6 empty] | Surface | Tube volume | Axial fan | [8 empty] | Connection |  | Fin Spacing | Drainage | Price
Refrigerant |  |  | R404A |  | Surface |  | 69 | m2 |  | Coil | Water tray | amount | TA…7 | L | W | H | B | E1 | E2 | E3 |  |  | Air Flow | Distance | Fan Speed |  | Diameter | Noise Level in 3M | Voltage | Input Power | Current | Liquid | Gas
Capacity |  |  | 40.66 | KW | Tube Volume |  | 21.3 | L |  | A | B | C | D | E | F | G | H | I | II | III | J | K | L | M | N |  | O | P | Q | R | S | T | U | V |  | X
Room Temp |  |  | 18 | °C | Fin Pitch |  | 7 | mm | KA-3003-7EB | 2x1590 | 1x1590 | 4770 | 66 | 2074 | 424 | 452 | 342 | 1829 | 600 | 1200 | 26 | 8 | 4260 | 11 | 1380 | 3 | 300 | 75 | 220V/1PH | 62 | 0.28 | 5/8" | 1-3/8" | 7 | G1" | 52000
Evaporation temp |  |  | 6 | °C | Test Pressure |  | 30 | Bar | KA-3503-7EB | 3x1875 | 1X1875 | 7500 | 86 | 2524 | 514 | 532 | 412 | 2279 | 750 | 1500 | 39 | 12 | 8340 | 10 | 1400 | 2 | 350 | 75 | 220V/1PH | 130 | 0.58 | 7/8" | 1-5/8" | 7 | G1.5" | 60000
Superheating |  |  | 5 | K |  |  |  |  | KA-4003-7EB | 3x1875 | 1X1875 | 7500 | 89 | 2544 | 514 | 532 | 346 | 2279 | 750 | 1500 | 39 | 12 | 9960 | 16 | 1380 | 3 | 400 | 82 | 220V/1PH | 160 | 0.7 | 7/8" | 1-5/8" | 7 | G1.5" | 65000
Condensation temp |  |  | 45 | °C |  |  |  |  | KA-4003-7EC | 4x1875 | 1X1875 | 9375 | 103.5 | 2544 | 514 | 532 | 412 | 2279 | 750 | 1500 | 59 | 18 | 9240 | 14 | 1430 | 3 | 400 | 82 | 220V/1PH | 160 | 0.7 | 7/8" | 1-5/8" | 7 | G1.5" | 82000
Suction gas temp |  |  | 20 | °C |  |  |  |  | KA-5003-7EB | 4x2300 | 1X2300 | 11500 | 151.5 | 3275 | 594 | 680 | 425 | 3030 | 1000 | 2000 | 69 | 21.3 | 21750 | 27 | 1430 | 3 | 500 | 88 | 380V/3PH | 820 | 1.59 | 7/8" | 1-5/8" | 7 | G1.5" | 125000
Subcooling |  |  | 0 | K |  |  |  |  | KA-5003-7EC | 6x2300 | 2X2300 | 18400 | 174 | 3275 | 594 | 680 | 491 | 3030 | 1000 | 2000 | 104 | 32.2 | 20640 | 25 | 1325 | 3 | 500 | 88 | 380V/3PH | 820 | 1.59 | 7/8" | 1-5/8" | 7 | G1.5" | 154000
[9 empty] | KA-3003-9EB | 2x1590 | 1x1590 | 4770 | 66 | 2074 | 424 | 452 | 342 | 1829 | 600 | 1200 | 21.23 | 8 | 4440 | 11 | 1380 | 3 | 300 | 75 | 220V/1PH | 62 | 0.28 | 5/8" | 1-3/8" | 9 | G1" | 52000
Fan Specification | [8 empty] | KA-4003-9EB | 3x1875 | 1X1875 | 7500 | 89 | 2544 | 514 | 532 | 346 | 2279 | 750 | 1500 | 31.89 | 12 | 10560 | 16 | 1430 | 3 | 400 | 82 | 220V/1PH | 160 | 0.7 | 7/8" | 1-5/8" | 9 | G1.5" | 65000
Air Flow |  |  | 21750 | m3/h | Voltage |  | 380V/3PH | V | KA-4003-9EC | 4x1875 | 1X1875 | 9375 | 103.5 | 2544 | 514 | 532 | 412 | 2279 | 750 | 1500 | 47.52 | 18 | 9960 | 14 | 1430 | 3 | 400 | 82 | 220V/1PH | 160 | 0.7 | 7/8" | 1-5/8" | 9 | G1.5" | 82000
Air Throw (approx) |  |  | 27 | m | Fan Speed |  | 1430 | rpm | KA-5003-9EB | 4x2300 | 1X2300 | 11500 | 151.5 | 3275 | 594 | 680 | 425 | 3030 | 1000 | 2000 | 56.78 | 21.3 | 22650 | 27 | 1325 | 3 | 500 | 88 | 380V/3PH | 820 | 1.59 | 7/8" | 1-5/8" | 9 | G1.5" | 125000
Fan Diameter |  |  | 500 | mm | Power |  | 820 | W | KA-5003-9EC | 6x2300 | 2X2300 | 18400 | 174 | 3275 | 594 | 680 | 491 | 3030 | 1000 | 2000 | 84.62 | 32.2 | 21060 | 25 | 1325 | 3 | 500 | 88 | 380V/3PH | 820 | 1.59 | 7/8" | 1-5/8" | 9 | G1.5" | 155000
Number of Fan |  |  | 3 |  | Current |  | 1.59 | Amp
[5 empty] | Noise Level 3 m |  | 88 | dBA
Tube Material |  |  | Copper |  | Inlet connection |  | 7/8" | inch
Fin Material |  |  | Aluminum |  | Outlet connection |  | 1-5/8" | inch
Casing Material |  |  | Powder-coated |  | Dry weight |  | 151.5 | kg |  | A: Air Inlet; B: 18; C: 10; D: 5; E: 0; F: -5; G: -10; H: -18; I: -25
[10 empty] | Evap Temp | 6 | 0 | -3 | -8 | -12 | -17 | -25 | -31
Dimension : | bar: B to I
L : | 3275 | [8 empty] | A: KA-3003-7EB; B: 11.44; C: 9.53; D: 7.63; E: 6.72; F: 5.86; G: 5.66; H: 5.34
E1 : | 3030 | [8 empty] | A: KA-3503-7EB; B: 14.8; C: 13; D: 11; E: 9.73; F: 8.48; G: 8.19; H: 7.75
E2 : | 1000 | [8 empty] | A: KA-4003-7EB; B: 22.52; C: 18.76; D: 15.01; E: 13.21; F: 11.51; G: 11.12; H: 10.49
E3 : | 2000 | [8 empty] | A: KA-4003-7EC; B: 27.84; C: 23.2; D: 18.56; E: 16.35; F: 14.24; G: 13.76; H: 12.98
H : | 680 | [8 empty] | A: KA-5003-7EB; B: 40.66; C: 33.89; D: 27.11; E: 23.89; F: 20.81; G: 20.11; H: 18.96
W : | 594 | [8 empty] | A: KA-5003-7EC; B: 51.11; C: 42.58; D: 34.07; E: 30.02; F: 26.15; G: 25.26; H: 23.83
B : | 425 | [8 empty] | A: KA-3003-9EB; B: 9.22; C: 7.84; D: 6.61; E: 6.31; F: 5.7; G: 5.61; H: 5.39; I: 4.35
[10 empty] | KA-4003-9EB | 16.56 | 14.07 | 11.87 | 11.32 | 10.23 | 10.07 | 9.68 | 7.81
[10 empty] | KA-4003-9EC | 20.84 | 17.71 | 14.94 | 14.25 | 12.88 | 12.68 | 12.19 | 9.83
Defrost | [9 empty] | A: KA-5003-9EB; B: 32.18; C: 27.35; D: 23.07; E: 22.01; F: 19.89; G: 19.58; H: 18.82; I: 15.18
Electric Defrost for Coil |  |  | 4x2300 | W |  | Drainage | G1.5" |  |  | A: KA-5003-9EC; B: 41.32; C: 35.12; D: 29.62; E: 28.26; F: 25.53; G: 25.14; H: 24.17; I: 19.49
Electric Defrost for Tray |  |  | 1X2300 | W |  | Price | 125000
Total |  |  | 11500 | W

## 4 พัดลม
[6 empty] | Software version : | Rel. 1.0.1.0 | [19 empty] | 0
[6 empty] | Date : | 2024-04-18
Project :
Quotation :
Air Cooler |  | Technical specifications ‐ Model : |  |  |  | KA-5004-9EC
Series : | KA
Capacity Information | [8 empty] | Model | Electrical Defrosing |  |  |  | Size | [7 empty] | Surface | Tube volume | Axial fan | [8 empty] | Connection |  | Fin Spacing | Price
Refrigerant |  |  | R404A
Capacity |  |  | 37.65 | Kw | Surface |  | 112.6 | m2 |  | Coil | Water tray | amount | TA…7 | L | W | H | B | E1 | E2 | E3 | E4 |  |  | Air Flow | Distance | Fan Speed |  | Diameter | Noise Level in 3M | Voltage | Input Power | Current | Liquid | Gas
Room Temp |  |  | 0 | °C | Tube Volume |  | 41 | L |  | A | B | C | D | E | F | G | H | I | II | III | IV | J | K | L | M | N |  | O | P | Q | R | S | T | U | V | W
Evaporation temp |  |  | -8 | °C | Fin Pitch |  | 9 | mm | KA-3004-7EB | 2x2120 | 1x2120 | 6360 | 88 | 2674 | 424 | 452 | 342 | 1829 | 600 | 1200 | 1800 | 34.3 | 10.6 | 5200 | 13 | 1380 | 4 | 300 | 76 | 220V/1PH | 62 | 0.28 | 5/8" | 1-3/8" | 7 | 75000
Superheating |  |  | 5 | K | Test Pressure |  | 30 | Bar | KA-4004-7EC | 4x2300 | 1X2300 | 11500 | 111 | 3274 | 514 | 532 | 412 | 3029 | 750 | 1500 | 2250 | 78 | 23.7 | 12320 | 17 | 1430 | 4 | 400 | 83 | 220V/1PH | 160 | 0.7 | 7/8" | 1-5/8" | 7 | 105000
Condensation temp |  |  | 45 | °C |  |  |  |  | KA-5004-7EB | 4x3180 | 1X3180 | 15900 | 187.5 | 4274 | 594 | 680 | 425 | 4030 | 1000 | 2000 | 3000 | 93 | 28.6 | 29000 | 30 | 1325 | 4 | 500 | 89 | 380V/3PH | 820 | 1.59 | 7/8" | 2-1/8" | 7 | 155000
Suction gas temp |  |  | 20 | °C |  |  |  |  | KA-5004-7EC | 6x3180 | 2X3180 | 25440 | 228 | 4274 | 594 | 680 | 491 | 4030 | 1000 | 2000 | 3000 | 139 | 41 | 27520 | 28 | 1325 | 4 | 500 | 89 | 380V/3PH | 820 | 1.59 | 1-1/8" | 2-1/8" | 7 | 204000
Subcooling |  |  | 0 | K |  |  |  |  | KA-3004-9EB | 2x2120 | 1x2120 | 6360 | 88 | 2674 | 424 | 452 | 342 | 1829 | 600 | 1200 | 1800 | 28.39 | 10.6 | 5920 | 13 | 1380 | 4 | 300 | 76 | 220V/1PH | 62 | 0.28 | 5/8" | 1-3/8" | 9 | 75000
[9 empty] | KA-4004-9EC | 4x2300 | 1X2300 | 11500 | 111 | 3274 | 514 | 532 | 412 | 3029 | 750 | 1500 | 2250 | 63.47 | 23.7 | 13280 | 17 | 1430 | 4 | 400 | 83 | 220V/1PH | 160 | 0.7 | 7/8" | 1-5/8" | 9 | 105000
Fan Specification | [8 empty] | KA-5004-9EB | 4x3180 | 1X3180 | 15900 | 187.5 | 4274 | 594 | 680 | 425 | 4030 | 1000 | 2000 | 3000 | 75.52 | 28.6 | 30200 | 30 | 1325 | 4 | 500 | 89 | 380V/3PH | 820 | 1.59 | 7/8" | 2-1/8" | 9 | 155000
Air Flow |  |  | 28040 | m3/h | Voltage |  | 380V/3PH |  | KA-5004-9EC | 6x3180 | 2X3180 | 25440 | 228 | 4274 | 594 | 680 | 491 | 4030 | 1000 | 2000 | 3000 | 112.6 | 41 | 28040 | 28 | 1325 | 4 | 500 | 89 | 380V/3PH | 820 | 1.59 | 1-1/8" | 2-1/8" | 9 | 204000
Air Throw (approx) |  |  | 28 | m | Fan Speed |  | 1325 | rpm
Fan Diameter |  |  | 500 | mm | Power |  | 820 | W
Number of Fan |  |  | 4 |  | Current |  | 1.59 | Amp
[5 empty] | Noise Level 3 m |  | 89 | dBA
[10 empty] | Air Inlet | 18 | 10 | 5 | 0 | -5 | -10 | -18 | -25
Tube Material |  |  | Copper |  | Inlet connection |  | 1-1/8" | inch |  | A: Evap Temp; B: 6; C: 0; D: -3; E: -8; F: -12; G: -17; H: -25; I: -31
Fin Material |  |  | Aluminum |  | Outlet connection |  | 2-1/8" | inch | bar: B to I
Casing Material |  |  | Powder-coated |  | Dry weight |  | 228 | kg |  | A: KA-3004-7EB; B: 15.09; C: 12.58; D: 10.08; E: 8.88; F: 6.91; G: 7.47; H: 7.05
[10 empty] | KA-4004-7EC | 36.92 | 30.76 | 24.61 | 21.68 | 18.89 | 18.24 | 17.21
Dimension : | [9 empty] | A: KA-5004-7EB; B: 53.53; C: 44.61; D: 35.69; E: 31.45; F: 27.39; G: 26.46; H: 24.96
L : | 4274 | [8 empty] | A: KA-5004-7EC; B: 68.49; C: 57.07; D: 45.66; E: 40.23; F: 35.04; G: 33.85; H: 31.93
E1 : | 4030 | [8 empty] | A: KA-3004-9EB; B: 12.32; C: 10.47; D: 8.83; E: 8.42; F: 7.61; G: 7.49; H: 7.19; I: 5.81
E2 : | 1000 | [8 empty] | A: KA-4004-9EC; B: 27.81; C: 23.64; D: 19.94; E: 19.02; F: 17.19; G: 16.92; H: 16.27; I: 13.12
E3 : | 2000 | [8 empty] | A: KA-5004-9EB; B: 42.85; C: 36.41; D: 30.72; E: 29.3; F: 26.48; G: 26.07; H: 25.06; I: 20.21
E4 : | 3000 | [8 empty] | A: KA-5004-9EC; B: 55.04; C: 46.77; D: 39.46; E: 37.65; F: 34.01; G: 33.49; H: 32.19; I: 25.96
H : | 680
W : | 594
B : | 491
Defrost
Electric Defrost for Coil |  |  | 6x3180 | W |  | Drainage | G1.5"
Electric Defrost for Tray |  |  | 2X3180 | W |  | Price | 204000
Total |  |  | 25440 | W